Sprinkler Inspection Certificate

For

|  | TAMPA SPORTS AUTHORITY |  |
| --- | --- | --- |
|  | 4201 N. DALE MABRY HWY |  |
|  | TAMPA, FL 33607 |  |

Tested to NFPA 25 Standards

This Inspection was performed in accordance with applicable NFPA Standards.  The subsequent pages of this report provide performance measurements, listed ranges of acceptable results, and complete documentation of the inspection.  Whenever discrepancies exist between acceptable performance standards and actual test results, notes and/or recommended solutions have been proposed or provided for immediate review and approval.

Inspection Date

Dec 22, 2020

| Building: TAMPA SPORTS AUTHORITY | Company: Fire & Life Safety America, Inc. - Tampa |
| --- | --- |
| Contact: Deltecia Jones | Contact: Tyson L. Mendel |
| Title: Procurement Manager | Title: Inspector |

Executive Summary

Generated by: BuildingReports.com

| Building Information |
| --- |
| Building: TAMPA SPORTS AUTHORITY | Contact: Deltecia Jones |
| Address: 4201 N. DALE MABRY HWY | Phone: 8133506511 |
| Address: | Fax: |
| City/State/Zip: TAMPA, FL 33607 | Mobile: |
| Country: United States of America | Email: djones@tampasportsauthority.com |
| Inspection Performed By |
| Company: Fire & Life Safety America, Inc. - Tampa | Inspector: Tyson L. Mendel |
| Address: 5915 Causeway Blvd | Phone: 813-513-9331 |
| Address: | Fax: |
| City/State/Zip: Tampa, FL 33619 | Mobile: 813-440-8475 |
| Country: United States of America | Email: tlmendel@flsamerica.com |
| System Control Unit |
| System Type | System Location | Protected Area | Devices |
| Fire Pump |  |  | 29 |
| Preaction |  | Control Room | 15 |
| Service Main |  |  | 9 |
| Standpipe |  | Quad A | 17 |
| Standpipe |  | Quad B | 19 |
| Standpipe |  | Quad C | 16 |
| Standpipe |  | Quad D | 24 |
| Standpipe |  | Stairway #6 | 22 |
| Standpipe |  | Stairway #7 | 27 |
| Wet Pipe |  |  | 2 |
| Wet Pipe |  | Pirate Ship | 12 |
| Wet Pipe |  | Quad A | 38 |
| Wet Pipe |  | Quad B | 14 |
| Wet Pipe |  | Quad C | 28 |
| Wet Pipe |  | Quad D | 7 |
| Wet Pipe |  | field | 1 |
| Wet Pipe |  | sideline | 1 |

| Inspection Summary |
| --- |
| Category | Total Items | Serviced | Passed | Failed/Other |
|  | Qty | % | Qty | % | Qty | % | Qty | % |
| Device | 39 | 13.88% | 39 | 100.00% | 39 | 100.00% | 0 | 0% |
| Alarm | 80 | 28.47% | 77 | 96.25% | 77 | 100.00% | 0 | 0% |
| Valve | 75 | 26.69% | 70 | 93.33% | 70 | 100.00% | 0 | 0% |
| Hose | 69 | 24.56% | 60 | 86.96% | 58 | 96.67% | 2 | 3.33% |
| Pump | 9 | 3.20% | 9 | 100.00% | 9 | 100.00% | 0 | 0% |
| Sprinkler | 9 | 3.20% | 5 | 55.56% | 5 | 100.00% | 0 | 0% |
| Totals | 281 | 100% | 260 | 92.53% | 258 | 99.23% | 2 | 0.77% |
| Certification |
| Company: Fire & Life Safety America, Inc. - Tampa | Building: TAMPA SPORTS AUTHORITY |
| Inspector: Tyson L. Mendel | Contact: Deltecia Jones |
| Signed: Dec 22, 2020 6:45:43 PM | Signed: Dec 22, 2020 1:10:22 PM |

Discrepancy Report

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |
| --- |
| The Discrepancy Report consolidates each discrepancy listed within the various Testing sections of your Inspection. Discrepancies are listed by Category, and grouped by device type. The description of the problem is provided and where appropriate, code references are listed for your convenience. Any item that was inspected that is subject to a recall or part of a manufacturer’s replacement/upgrade program is included. |
| Device Type | Manufacturer | ModelNumber | Date | Qty |
| Items listed for Recall or Replacement/Upgrade |
| No items found during this inspection. |

| & ScanID | ` Location | L Problem | & Reference |
| --- | --- | --- | --- |
| Standpipe, Quad A |
| Critical Deficiencies |
| Fire Dep't Connection |
| 49546380 | Quad A FDC | Rusted/Corroded | NFPA25 13.7.1 (2) (3) |
| Standpipe, Stairway #7 |
| Hose Connection |
| 49546410 | 1st Stairway #7 | Leaking | NFPA25 4.1.5.1 |
| Code References |
| NFPA25 13.7.1 (2) (3) | Fire department connections shall be inspected quarterly to verify the following: Couplings or swivels are not damaged and rotate smoothly. Plugs or caps are in place and undamaged. |
| NFPA25 4.1.5.1 | The property owner or designated representative shall correct or repair deficiencies or impairments that are found during the inspection, test, and maintenance required by this standard. |

Proposed Solutions Report

Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY

The Proposed Solution Report provides a solution for each discrepancy listed on the Discrepancy Report. Provide a check mark where indicated to approve repairs listed within the report. Items listed as T/M are available for repair on a Time and Materials basis.

| ScanID | Location | Solution | Model # | Cost | Fix |
| --- | --- | --- | --- | --- | --- |
| Standpipe, Quad A |
| Critical Deficiencies |
| Fire Dep't Connection |
| 49546380 | Quad A FDC | Replace | unknown | T/M | ¨ |
| Standpipe, Stairway #7 |
| Hose Connection |
| 49546410 | 1st Stairway #7 | Correct | unknown | T/M | ¨ |
| PO #: (none) | T/M |  |

Inspection & Testing

Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY

The Inspection & Testing section lists all of the items inspected in your building. Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.

| Device Type | Location | Service | Time | Date |
| --- | --- | --- | --- | --- |
| Passed |
| Fire Pump |
| Tamper Switch | Fire Pump Suction | Quarterly | 7:42:23 AM | 12/22/2020 |
| Tamper Switch | Fire Pump Test Header | Quarterly | 7:48:05 AM | 12/22/2020 |
| Tamper Switch | Fire Pump Discharge | Quarterly | 7:48:50 AM | 12/22/2020 |
| Tamper Switch | Fire Pump Bypass | Quarterly | 7:50:36 AM | 12/22/2020 |
| Tamper Switch | Fire Pump Bypass | Quarterly | 7:51:15 AM | 12/22/2020 |
| Gauge | Fire Pump Controller | Quarterly | 7:42:29 AM | 12/22/2020 |
| Gauge | Fire Pump Relief Valve | Quarterly | 7:45:40 AM | 12/22/2020 |
| Gauge | Fire Pump Relief Valve | Quarterly | 7:46:03 AM | 12/22/2020 |
| Gauge | Jockey Pump Discharge | Quarterly | 7:49:03 AM | 12/22/2020 |
| Gauge | Jockey Pump Controller | Quarterly | 7:49:32 AM | 12/22/2020 |
| Gauge | Jockey Pump Suction | Quarterly | 7:49:44 AM | 12/22/2020 |
| Gauge | Jockey Pump Controller | Quarterly | 7:51:54 AM | 12/22/2020 |
| Controller | Pump Room | Quarterly | 7:43:18 AM | 12/22/2020 |
| Electrical Driver | Fire Pump Room | Quarterly | 7:43:54 AM | 12/22/2020 |
| Fire Pump Gauge | Jockey Pump Discharge | Quarterly | 7:44:20 AM | 12/22/2020 |
| Fire Pump Gauge | Jockey Pump Discharge | Quarterly | 7:45:36 AM | 12/22/2020 |
| Jockey Controller | Jockey Pump Controller | Quarterly | 7:51:48 AM | 12/22/2020 |
| Jockey Pump | Fire Pump Room | Quarterly | 7:49:38 AM | 12/22/2020 |
| Pump | Fire Pump Room | Quarterly | 6:49:18 PM | 12/22/2020 |
| Signage | Control Room | Quarterly | 12:56:32 PM | 12/22/2020 |
| Signage | Home Team Locker Room | Quarterly | 12:56:33 PM | 12/22/2020 |
| Signage | Team Store Atrium | Quarterly | 12:56:35 PM | 12/22/2020 |
| Control Valve | Fire Pump Suction | Quarterly | 7:42:22 AM | 12/22/2020 |
| Control Valve | Fire Pump Test Header | Quarterly | 7:47:52 AM | 12/22/2020 |
| Control Valve | Jockey Pump Discharge | Quarterly | 7:48:43 AM | 12/22/2020 |
| Control Valve | Fire Pump Discharge | Quarterly | 7:49:02 AM | 12/22/2020 |
| Control Valve | Jockey Pump Suction | Quarterly | 7:50:13 AM | 12/22/2020 |
| Control Valve | Fire Pump Bypass | Quarterly | 7:50:29 AM | 12/22/2020 |
| Control Valve | Fire Pump Bypass | Quarterly | 7:51:28 AM | 12/22/2020 |
| Preaction, Control Room |
| Control Panel | Upper Suite A Control Room | Quarterly | 12:06:06 PM | 12/22/2020 |
| Pressure Switch | Upper Suite A Control Room Pressure Switch | Quarterly | 12:11:18 PM | 12/22/2020 |
| Pressure Switch | Control Room Alarm Air Pressure | Quarterly | 12:14:01 PM | 12/22/2020 |
| Tamper Switch | Control Room Low Air | Quarterly | 12:08:25 PM | 12/22/2020 |
| Drain | Control Room | Quarterly | 12:14:59 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:09:34 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:09:59 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:10:15 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:10:33 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:10:58 PM | 12/22/2020 |
| Gauge | Control Room | Quarterly | 12:13:19 PM | 12/22/2020 |
| Air Compressor | Control Room Low Air | Quarterly | 12:14:34 PM | 12/22/2020 |
| Air Maintenance Device | Control Room | Quarterly | 12:13:33 PM | 12/22/2020 |
| Control Valve | Upper Suite A Control Room Main Control | Quarterly | 12:07:49 PM | 12/22/2020 |
| Preaction Valve | Control Room | Quarterly | 12:08:42 PM | 12/22/2020 |
| Standpipe, Quad A |
| Tamper Switch | Quad A Housekeeping / Field Entry M1-9 | Quarterly | 8:02:19 AM | 12/22/2020 |
| Tamper Switch | Quad A Housekeeping / Ramp M1-50 | Quarterly | 8:03:32 AM | 12/22/2020 |
| Tamper Switch | Quad A Mechanical Room M1-22 | Quarterly | 8:04:49 AM | 12/22/2020 |
| Hose Connection | 2nd Quad A Main Concourse | Quarterly | 9:45:59 AM | 12/22/2020 |
| Hose Connection | 4th Quad A Club Level | Quarterly | 11:51:13 AM | 12/22/2020 |
| Hose Connection | 5th Quad A Lower Suite | Quarterly | 11:57:58 AM | 12/22/2020 |
| Hose Connection | 6th Quad A Upper Suite | Quarterly | 12:04:27 PM | 12/22/2020 |
| Hose Connection | 7th Quad A Upper Concourse | Quarterly | 10:07:08 AM | 12/22/2020 |
| Hose Connection | Quad A Catering Warehouse | Quarterly | 7:59:26 AM | 12/22/2020 |
| Hose Connection | Quad A Ramp | Quarterly | 8:03:05 AM | 12/22/2020 |
| Hose Connection | Quad A Mechanical Room | Quarterly | 8:04:45 AM | 12/22/2020 |
| Hose Connection | Quad A Players Corridor | Quarterly | 8:10:17 AM | 12/22/2020 |
| Hose Connection | Quad A Field Entry | Quarterly | 8:49:58 AM | 12/22/2020 |
| Control Valve | Quad A Housekeeping / Field Entry M1-9 | Quarterly | 8:02:27 AM | 12/22/2020 |
| Control Valve | Quad A Housekeeping / Ramp M1-50 | Quarterly | 8:03:47 AM | 12/22/2020 |
| Control Valve | Quad A Mechanical Room M1-22 | Quarterly | 8:05:00 AM | 12/22/2020 |
| Standpipe, Quad B |
| Tamper Switch | Quad B Delivery Swing Gate M1-49 | Quarterly | 8:53:51 AM | 12/22/2020 |
| Tamper Switch | Quad B Chiller M1-47 | Quarterly | 8:55:21 AM | 12/22/2020 |
| Fire Dep't Connection | Quad B FDC | Quarterly | 7:22:31 AM | 12/22/2020 |
| Hose Connection | 2nd Quad B Main Concourse | Quarterly | 9:32:59 AM | 12/22/2020 |
| Hose Connection | 4th Quad B / C Club Level | Quarterly | 11:27:51 AM | 12/22/2020 |
| Hose Connection | 4th Quad B Club Level | Quarterly | 12:30:04 PM | 12/22/2020 |
| Hose Connection | 5th Quad B / C Lower Suite | Quarterly | 11:30:12 AM | 12/22/2020 |
| Hose Connection | 5th Quad B Lower Suite | Quarterly | 12:32:00 PM | 12/22/2020 |
| Hose Connection | 6th Quad B / C Ford Super Suite | Quarterly | 11:32:46 AM | 12/22/2020 |
| Hose Connection | 6th Quad B Ford Super Suite Pantry / Stairway 2 | Quarterly | 12:39:05 PM | 12/22/2020 |
| Hose Connection | 7th Quad B Upper Concourse | Quarterly | 10:53:43 AM | 12/22/2020 |
| Hose Connection | Quad B Delivery Swing Gate | Quarterly | 7:53:34 AM | 12/22/2020 |
| Hose Connection | Quad B Field Entry | Quarterly | 8:39:46 AM | 12/22/2020 |
| Hose Connection | Quad B East Club/Suite Lobby Hall | Quarterly | 8:40:48 AM | 12/22/2020 |
| Hose Connection | Quad B Chiller | Quarterly | 8:55:10 AM | 12/22/2020 |
| Control Valve | Quad B Delivery Swing Gate M1-49 | Quarterly | 7:52:56 AM | 12/22/2020 |
| Control Valve | Quad B Chiller M1-47 | Quarterly | 8:55:35 AM | 12/22/2020 |
| Standpipe, Quad C |
| Tamper Switch | Quad C Tunnel / Grounds Crew M1-26 | Quarterly | 8:34:09 AM | 12/22/2020 |
| Tamper Switch | Quad C Middle Hall M1-24 | Quarterly | 8:42:12 AM | 12/22/2020 |
| Tamper Switch | Quad C Mechanical M1-34 | Quarterly | 11:13:23 AM | 12/22/2020 |
| Fire Dep't Connection | Quad C FDC | Quarterly | 9:12:19 AM | 12/22/2020 |
| Hose Connection | 2nd Quad C Main Concourse | Quarterly | 9:35:03 AM | 12/22/2020 |
| Hose Connection | 4th Quad C Club Level | Quarterly | 12:48:46 PM | 12/22/2020 |
| Hose Connection | 5th Quad C Lower Suite | Quarterly | 12:48:06 PM | 12/22/2020 |
| Hose Connection | 6th Quad C Upper Suite | Quarterly | 12:44:43 PM | 12/22/2020 |
| Hose Connection | 7th Quad C Upper Concourse | Quarterly | 10:55:06 AM | 12/22/2020 |
| Hose Connection | Quad C Tunnel / Grounds Crew | Quarterly | 8:34:41 AM | 12/22/2020 |
| Hose Connection | Quad C Mechanical | Quarterly | 8:35:58 AM | 12/22/2020 |
| Hose Connection | Quad C Field Entry | Quarterly | 8:38:16 AM | 12/22/2020 |
| Hose Connection | Quad C Middle Hall | Quarterly | 8:41:23 AM | 12/22/2020 |
| Control Valve | Quad C Tunnel / Grounds Crew M1-26 | Quarterly | 8:34:18 AM | 12/22/2020 |
| Control Valve | Quad C Middle Hall M1-24 | Quarterly | 8:42:08 AM | 12/22/2020 |
| Control Valve | Quad C Mechanical M1-34 | Quarterly | 9:17:27 AM | 12/22/2020 |
| Standpipe, Quad D |
| Tamper Switch | Quad D Players Entrance M1-25 | Quarterly | 8:11:43 AM | 12/22/2020 |
| Tamper Switch | Quad D Roll Up Door M1-27 | Quarterly | 8:26:12 AM | 12/22/2020 |
| Tamper Switch | Quad D Mechanical M1-30 | Quarterly | 8:27:04 AM | 12/22/2020 |
| Tamper Switch | Quad D TSA Hall M1-29 | Quarterly | 8:32:56 AM | 12/22/2020 |
| Tamper Switch | Quad D Buccs Warehouse HR Door 2 locker | Quarterly | 11:16:21 AM | 12/22/2020 |
| Fire Dep't Connection | Quad D FDC | Quarterly | 9:08:41 AM | 12/22/2020 |
| Hose Connection | 2nd Quad D Main Concourse | Quarterly | 9:44:43 AM | 12/22/2020 |
| Hose Connection | 4th Quad A / D Club Level | Quarterly | 11:53:22 AM | 12/22/2020 |
| Hose Connection | 4th Quad D Club Level | Quarterly | 11:54:23 AM | 12/22/2020 |
| Hose Connection | 5th Quad A / D Lower Suite | Quarterly | 11:59:34 AM | 12/22/2020 |
| Hose Connection | 5th Quad D Lower Suite | Quarterly | 12:00:29 PM | 12/22/2020 |
| Hose Connection | 6th Quad D | Quarterly | 10:14:47 AM | 12/22/2020 |
| Hose Connection | 6th Quad A / D Press Box | Quarterly | 12:18:06 PM | 12/22/2020 |
| Hose Connection | 6th Quad D Press Box | Quarterly | 12:21:15 PM | 12/22/2020 |
| Hose Connection | Quad D Players Corridor | Quarterly | 8:10:47 AM | 12/22/2020 |
| Hose Connection | Quad D Roll Up Door | Quarterly | 8:23:57 AM | 12/22/2020 |
| Hose Connection | Quad D TSA Hall | Quarterly | 8:32:29 AM | 12/22/2020 |
| Hose Connection | Quad D Field Entry | Quarterly | 8:48:16 AM | 12/22/2020 |
| Hose Connection | Quad D Mechanical | Quarterly | 9:18:30 AM | 12/22/2020 |
| Control Valve | Quad D Players Entrance M1-25 | Quarterly | 8:11:36 AM | 12/22/2020 |
| Control Valve | Quad D Roll Up Door M1-27 | Quarterly | 8:26:22 AM | 12/22/2020 |
| Control Valve | Quad D Mechanical M1-30 | Quarterly | 8:27:15 AM | 12/22/2020 |
| Control Valve | Quad D TSA Hall M1-29 | Quarterly | 8:33:06 AM | 12/22/2020 |
| Control Valve | Quad D Buccs Warehouse HR Door 2 locker | Quarterly | 11:16:10 AM | 12/22/2020 |
| Standpipe, Stairway #6 |
| Tamper Switch | 2nd Stairway #6 M2-15 | Quarterly | 11:08:45 AM | 12/22/2020 |
| Tamper Switch | 3rd Stairway #6 M2-14 | Quarterly | 11:08:05 AM | 12/22/2020 |
| Tamper Switch | 4th Stairway #7 M2-13 Club Level | Quarterly | 11:07:24 AM | 12/22/2020 |
| Tamper Switch | 5th Stairway #6 M2-24 Lower Suite | Quarterly | 11:06:36 AM | 12/22/2020 |
| Tamper Switch | 6th Stairway #6 M2-35 Upper Suite | Quarterly | 11:05:35 AM | 12/22/2020 |
| Waterflow Switch | 4th Stairway #6 Club Level | Quarterly | 11:07:21 AM | 12/22/2020 |
| Waterflow Switch | 5th Stairway #6 Lower Suite | Quarterly | 11:06:30 AM | 12/22/2020 |
| Waterflow Switch | 6th Stairway #6 Upper Suite | Quarterly | 11:05:25 AM | 12/22/2020 |
| Gauge | 7th Stairway #6 | Quarterly | 11:04:33 AM | 12/22/2020 |
| Hose Connection | 1st Stairway #6 | Quarterly | 11:10:54 AM | 12/22/2020 |
| Hose Connection | 3rd Stairway #6 | Quarterly | 11:07:59 AM | 12/22/2020 |
| Hose Connection | 4th Stairway #6 | Quarterly | 11:07:35 AM | 12/22/2020 |
| Hose Connection | 5th Stairway #6 | Quarterly | 11:06:45 AM | 12/22/2020 |
| Hose Connection | 7th Stairway #6 | Quarterly | 11:04:30 AM | 12/22/2020 |
| Control Valve | 2nd Stairway #6 M2-15 | Quarterly | 11:08:53 AM | 12/22/2020 |
| Control Valve | 3rd Stairway #6 M2-14 | Quarterly | 11:08:20 AM | 12/22/2020 |
| Control Valve | 4th Stairway #7 M2-13 Club Level | Quarterly | 11:07:31 AM | 12/22/2020 |
| Control Valve | 5th Stairway #6 M2-24 Lower Suite | Quarterly | 11:06:43 AM | 12/22/2020 |
| Control Valve | 6th Stairway #6 M2-35 Upper Suite | Quarterly | 11:05:46 AM | 12/22/2020 |
| Inspector's Test | 4th Stairway #6 Club Level | Quarterly | 11:07:04 AM | 12/22/2020 |
| Inspector's Test | 5th Stairway #6 Lower Suite | Quarterly | 11:06:23 AM | 12/22/2020 |
| Inspector's Test | 6th Stairway #6 Upper Suite | Quarterly | 11:05:10 AM | 12/22/2020 |
| Standpipe, Stairway #7 |
| Tamper Switch | 2nd Stairway #7 M2-5 | Quarterly | 10:28:45 AM | 12/22/2020 |
| Tamper Switch | 3rd Stairway #7 M2-29 | Quarterly | 10:28:05 AM | 12/22/2020 |
| Tamper Switch | 4th Stairway #7 M2-7 Club Level | Quarterly | 10:25:36 AM | 12/22/2020 |
| Tamper Switch | 5th Stairway #7 M2-7 Lower Suite | Quarterly | 10:23:46 AM | 12/22/2020 |
| Tamper Switch | 6th Stairway #7 M2-57 Upper Suite | Quarterly | 10:24:19 AM | 12/22/2020 |
| Waterflow Switch | 4th Stairway #7 M2-99 Club Level | Quarterly | 10:24:59 AM | 12/22/2020 |
| Waterflow Switch | 5th Stairway #7 Lower Suite | Quarterly | 10:23:16 AM | 12/22/2020 |
| Waterflow Switch | 6th Stairway #7 Upper Suite | Quarterly | 10:21:14 AM | 12/22/2020 |
| Gauge | 4th Stairway #7 M2-99 Atrium | Quarterly | 10:25:57 AM | 12/22/2020 |
| Gauge | 7th Stairway #7 | Quarterly | 10:20:24 AM | 12/22/2020 |
| Hose Connection | 5th Stairway #7 | Quarterly | 10:23:04 AM | 12/22/2020 |
| Hose Connection | 6th Stairway #7 | Quarterly | 10:21:08 AM | 12/22/2020 |
| Hose Connection | 7th Stairway #7 | Quarterly | 10:20:09 AM | 12/22/2020 |
| Hose Connection | 7th Stairway #7 | Quarterly | 10:20:18 AM | 12/22/2020 |
| Control Valve | 2nd Stairway #7 M2-5 | Quarterly | 10:28:41 AM | 12/22/2020 |
| Control Valve | 3rd Stairway #7 M2-29 | Quarterly | 10:27:57 AM | 12/22/2020 |
| Control Valve | 4th Stairway #7 M2-7 Club Level | Quarterly | 10:25:47 AM | 12/22/2020 |
| Control Valve | 4th Stairway #7 M2-99 Atrium | Quarterly | 10:26:29 AM | 12/22/2020 |
| Control Valve | 5th Stairway #7 M2-7 Lower Suite | Quarterly | 10:23:59 AM | 12/22/2020 |
| Control Valve | 6th Stairway #7 M2-57 Upper Suite | Quarterly | 10:24:22 AM | 12/22/2020 |
| Inspector's Test | 4th Stairway #7 Club Level | Quarterly | 10:25:03 AM | 12/22/2020 |
| Inspector's Test | 5th Stairway #7 Lower Suite | Quarterly | 10:23:30 AM | 12/22/2020 |
| Inspector's Test | 6th Stairway #7 Upper Suite | Quarterly | 10:21:27 AM | 12/22/2020 |
| Wet Pipe, field |
| Hose Connection | East sideline on field | Quarterly | 8:38:45 AM | 12/22/2020 |
| Wet Pipe, Pirate Ship |
| Tamper Switch | Under Ship M-46 | Quarterly | 9:21:34 AM | 12/22/2020 |
| Waterflow Switch | Under Ship | Quarterly | 9:23:36 AM | 12/22/2020 |
| Drain | Under Ship | Quarterly | 9:23:56 AM | 12/22/2020 |
| Gauge | Under Ship | Quarterly | 9:22:06 AM | 12/22/2020 |
| Gauge | Under Ship | Quarterly | 9:22:46 AM | 12/22/2020 |
| Alarm Valve | Under Ship | Quarterly | 9:21:13 AM | 12/22/2020 |
| Control Valve | Under Ship M-46 | Quarterly | 9:21:31 AM | 12/22/2020 |
| Inspector's Test | Under Ship | Quarterly | 9:23:40 AM | 12/22/2020 |
| Wet Pipe, Quad A |
| Tamper Switch | 2nd Quad A Main Concourse M1-51 | Quarterly | 9:47:13 AM | 12/22/2020 |
| Tamper Switch | 2nd Quad A Main Concourse M1-41 | Quarterly | 9:49:51 AM | 12/22/2020 |
| Tamper Switch | 7th Quad A Upper Concourse M2-75 | Quarterly | 10:10:00 AM | 12/22/2020 |
| Tamper Switch | Quad A Catering Warehouse Restroom / Kitchen M1- | Quarterly | 8:01:20 AM | 12/22/2020 |
| Tamper Switch | Quad A Undeveloped Space M1-21 | Quarterly | 8:08:14 AM | 12/22/2020 |
| Tamper Switch | Quad A Undeveloped Space | Quarterly | 8:08:20 AM | 12/22/2020 |
| Tamper Switch | Quad A Owners Parking M1-16 | Quarterly | 8:16:29 AM | 12/22/2020 |
| Tamper Switch | Quad A Catering Warehouse M1-76 | Quarterly | 8:51:57 AM | 12/22/2020 |
| Waterflow Switch | 2nd Quad A Main Concourse | Quarterly | 9:49:44 AM | 12/22/2020 |
| Waterflow Switch | 7th Quad A Upper Concourse | Quarterly | 10:10:09 AM | 12/22/2020 |
| Waterflow Switch | Quad A Undeveloped Space | Quarterly | 8:08:25 AM | 12/22/2020 |
| Waterflow Switch | Quad A Undeveloped Space | Quarterly | 8:08:32 AM | 12/22/2020 |
| Waterflow Switch | Quad A Owners Parking | Quarterly | 8:16:13 AM | 12/22/2020 |
| Drain | 2nd Quad A Main Concourse M1-41 | Quarterly | 9:47:42 AM | 12/22/2020 |
| Drain | 2nd Quad A Main Concourse M1-41 | Quarterly | 9:50:09 AM | 12/22/2020 |
| Drain | 7th Quad A Upper Concourse | Quarterly | 10:09:24 AM | 12/22/2020 |
| Gauge | 2nd Quad A Main Concourse | Quarterly | 9:48:03 AM | 12/22/2020 |
| Gauge | 2nd Quad A Main Concourse | Quarterly | 9:48:24 AM | 12/22/2020 |
| Gauge | 2nd Quad A Main Concourse | Quarterly | 9:50:40 AM | 12/22/2020 |
| Gauge | 2nd Quad A Main Concourse | Quarterly | 9:51:06 AM | 12/22/2020 |
| Gauge | 7th Quad A Upper Concourse | Quarterly | 10:08:28 AM | 12/22/2020 |
| Gauge | 7th Quad A Upper Concourse | Quarterly | 10:08:54 AM | 12/22/2020 |
| Gauge | Quad A Owners Parking | Quarterly | 8:15:35 AM | 12/22/2020 |
| Signage | Quad A Owners Parking RJ Corridor | Quarterly | 8:16:38 AM | 12/22/2020 |
| Signage | Quad A Owners Parking RJ Parking | Quarterly | 8:16:52 AM | 12/22/2020 |
| Alarm Valve | 2nd Quad A Main Concourse | Quarterly | 9:47:35 AM | 12/22/2020 |
| Alarm Valve | 2nd Quad A Main Concourse | Quarterly | 9:50:30 AM | 12/22/2020 |
| Alarm Valve | 7th Quad A Upper Concourse | Quarterly | 10:08:24 AM | 12/22/2020 |
| Control Valve | 2nd Quad A Main Concourse M1-51 | Quarterly | 9:47:10 AM | 12/22/2020 |
| Control Valve | 2nd Quad A Main Concourse M1-41 | Quarterly | 9:50:01 AM | 12/22/2020 |
| Control Valve | 7th Quad A Upper Concourse M2-75 | Quarterly | 10:09:57 AM | 12/22/2020 |
| Control Valve | Quad A Catering Warehouse Restroom / Kitchen M1- | Quarterly | 8:01:32 AM | 12/22/2020 |
| Control Valve | Quad A Undeveloped Space M1-21 | Quarterly | 8:08:42 AM | 12/22/2020 |
| Control Valve | Quad A Undeveloped Space M1-19 | Quarterly | 8:08:50 AM | 12/22/2020 |
| Control Valve | Quad A Owners Parking M1-16 | Quarterly | 8:16:26 AM | 12/22/2020 |
| Control Valve | Quad A Catering Warehouse M1-76 | Quarterly | 8:52:10 AM | 12/22/2020 |
| Inspector's Test | Quad A Owners Parking | Quarterly | 8:18:37 AM | 12/22/2020 |
| Wet Pipe, Quad B |
| Tamper Switch | Quad B Engineering M1-33 | Quarterly | 7:40:37 AM | 12/22/2020 |
| Tamper Switch | Quad B Boiler M1-38 | Quarterly | 7:55:06 AM | 12/22/2020 |
| Tamper Switch | Quad B Boiler M1-39 | Quarterly | 7:55:21 AM | 12/22/2020 |
| Tamper Switch | Quad B Food Vending M1-40 | Quarterly | 7:56:37 AM | 12/22/2020 |
| Tamper Switch | Quad B Food Vending M1-37 | Quarterly | 7:56:43 AM | 12/22/2020 |
| Tamper Switch | Quad B East Club/Suite Lobby Hall M1-35 | Quarterly | 8:58:24 AM | 12/22/2020 |
| Waterflow Switch | Quad B East Club/Suite Lobby Hall | Quarterly | 8:58:43 AM | 12/22/2020 |
| Waterflow Switch | Quad B East Club/Suite Lobby Hall | Quarterly | 8:58:47 AM | 12/22/2020 |
| Control Valve | Quad B Engineering M1-33 | Quarterly | 7:41:09 AM | 12/22/2020 |
| Control Valve | Quad B Boiler M1-38 | Quarterly | 7:55:18 AM | 12/22/2020 |
| Control Valve | Quad B Boiler M1-39 | Quarterly | 7:55:33 AM | 12/22/2020 |
| Control Valve | Quad B Food Vending M1-37 | Quarterly | 7:57:00 AM | 12/22/2020 |
| Control Valve | Quad B Food Vending M1-40 | Quarterly | 7:57:08 AM | 12/22/2020 |
| Control Valve | Quad B East Club/Suite Lobby Hall M1-35 | Quarterly | 8:58:40 AM | 12/22/2020 |
| Wet Pipe, Quad C |
| Tamper Switch | 2nd Quad C Main Concourse M1-45 | Quarterly | 9:35:56 AM | 12/22/2020 |
| Tamper Switch | 2nd Quad C Main Concourse M1-45 | Quarterly | 9:38:17 AM | 12/22/2020 |
| Tamper Switch | 7th Quad C Upper Concourse M2-46 | Quarterly | 10:56:08 AM | 12/22/2020 |
| Tamper Switch | Quad C Grounds Crew Storage Cage M1-29 | Quarterly | 8:44:49 AM | 12/22/2020 |
| Tamper Switch | Quad C Grounds Crew Storage Cage M1-30 | Quarterly | 8:45:08 AM | 12/22/2020 |
| Waterflow Switch | 2nd Quad C Main Concourse M-46 | Quarterly | 9:36:13 AM | 12/22/2020 |
| Waterflow Switch | 2nd Quad C Main Concourse M-50 | Quarterly | 9:39:08 AM | 12/22/2020 |
| Waterflow Switch | 7th Quad C Upper Concourse | Quarterly | 10:57:10 AM | 12/22/2020 |
| Waterflow Switch | Quad C Grounds Crew Storage Cage | Quarterly | 8:44:53 AM | 12/22/2020 |
| Waterflow Switch | Quad C Grounds Crew Storage Cage | Quarterly | 8:45:11 AM | 12/22/2020 |
| Drain | 2nd Quad C Main Concourse | Quarterly | 9:39:26 AM | 12/22/2020 |
| Drain | 2nd Quad C Main Concourse | Quarterly | 9:39:41 AM | 12/22/2020 |
| Drain | 7th Quad C Upper Concourse | Quarterly | 11:18:44 AM | 12/22/2020 |
| Gauge | 2nd Quad C Main Concourse | Quarterly | 9:36:33 AM | 12/22/2020 |
| Gauge | 2nd Quad C Main Concourse | Quarterly | 9:37:36 AM | 12/22/2020 |
| Gauge | 2nd Quad C Main Concourse | Quarterly | 9:38:28 AM | 12/22/2020 |
| Gauge | 2nd Quad C Main Concourse | Quarterly | 9:38:45 AM | 12/22/2020 |
| Gauge | 7th Quad C Upper Concourse | Quarterly | 10:56:32 AM | 12/22/2020 |
| Gauge | 7th Quad C Upper Concourse | Quarterly | 10:56:53 AM | 12/22/2020 |
| Alarm Valve | 2nd Quad C Main Concourse M1-45 | Quarterly | 9:36:09 AM | 12/22/2020 |
| Alarm Valve | 2nd Quad C Main Concourse M-50 | Quarterly | 9:38:25 AM | 12/22/2020 |
| Alarm Valve | 7th Quad C Upper Concourse | Quarterly | 10:56:26 AM | 12/22/2020 |
| Control Valve | 2nd Quad C Main Concourse M1-45 | Quarterly | 9:35:53 AM | 12/22/2020 |
| Control Valve | 2nd Quad C Main Concourse M1-45 | Quarterly | 9:38:11 AM | 12/22/2020 |
| Control Valve | 7th Quad C Upper Concourse M2-46 | Quarterly | 10:56:16 AM | 12/22/2020 |
| Control Valve | Quad C Grounds Crew Storage Cage M1-29 | Quarterly | 8:44:45 AM | 12/22/2020 |
| Control Valve | Quad C Grounds Crew Storage Cage M1-30 | Quarterly | 8:45:05 AM | 12/22/2020 |
| Wet Pipe, Quad D |
| Tamper Switch | Quad D Roll Up Door M1-28 | Quarterly | 8:24:44 AM | 12/22/2020 |
| Tamper Switch | Quad D TSA Hall M-119 | Quarterly | 8:31:28 AM | 12/22/2020 |
| Waterflow Switch | 2nd Quad A Main Concourse | Quarterly | 9:50:38 AM | 12/22/2020 |
| Waterflow Switch | Quad D Roll Up Door | Quarterly | 8:24:48 AM | 12/22/2020 |
| Waterflow Switch | Quad D TSA Hall | Quarterly | 8:31:33 AM | 12/22/2020 |
| Control Valve | Quad D Roll Up Door M1-28 | Quarterly | 8:25:00 AM | 12/22/2020 |
| Control Valve | Quad D TSA Hall M-119 | Quarterly | 8:31:24 AM | 12/22/2020 |
| Wet Pipe, sideline |
| Hose Connection | West sideline on field | Quarterly | 8:49:02 AM | 12/22/2020 |
| Wet Pipe |
| Waterflow Switch | Quad D owner storage warehouse M1-19 | Quarterly | 11:16:25 AM | 12/22/2020 |
| Failed/Other |
| Standpipe, Quad A |
| Fire Dep't Connection | Quad A FDC | Quarterly | 9:07:23 AM | 12/22/2020 |
| Standpipe, Stairway #7 |
| Hose Connection | 1st Stairway #7 | Quarterly | 10:33:58 AM | 12/22/2020 |
| Untested |
| Service Main |
| Fire Hydrant | Southeast |  |  |  |
| Fire Hydrant | Northeast |  |  |  |
| Fire Hydrant | Quad B |  |  |  |
| Fire Hydrant | Quad A |  |  |  |
| Fire Hydrant | Quad A |  |  |  |
| Fire Hydrant | West Hyundai Club |  |  |  |
| Fire Hydrant | West team store |  |  |  |
| Fire Hydrant | Quad D |  |  |  |
| Fire Hydrant | Quad C |  |  |  |
| Standpipe, Quad B |
| Tamper Switch | Quad B East Club/Suite Lobby Hall M1-15 |  |  |  |
| Control Valve | Quad B East Club/Suite Lobby Hall M1-15 |  |  |  |
| Standpipe, Stairway #7 |
| Tamper Switch | 4th Stairway #7 M2-99 Atrium |  |  |  |
| Waterflow Switch | 4th Stairway #7 M2-99 Atrium |  |  |  |
| Inspector's Test | 4th Stairway #7 M2-99 Atrium |  |  |  |
| Wet Pipe, Pirate Ship |
| Special Sprinkler | Under Ship |  |  |  |
| Sprinkler Box | Under Ship |  |  |  |
| Sprinkler Box Spares | Under Ship |  |  |  |
| Wrenches | Under Ship |  |  |  |
| Wet Pipe, Quad A |
| Inspector's Test | Quad A Undeveloped Space M1-19 |  |  |  |
| Wet Pipe, Quad C |
| Inspector's Test | 7th Quad C Upper Concourse Men’s restroom 330-331 |  |  |  |
| Wet Pipe |
| Inspector's Test | Quad D owner storage warehouse M1-19 |  |  |  |

Wet Pipe Fire Sprinkler Systems

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |  |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | unknown | unknown |  | 6" | 1 | þ | 57508119 |
| Components |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown | 175 | 36 |  | ¨ | 42761839 |
| Location |
| Quad D owner storage warehouse M1-19 |

| Building: TAMPA SPORTS AUTHORITY | Pirate Ship |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| OS&Y | Supervisory | System Sensor | 1 | þ | 49546384 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | Potter | OVSR |  | 4” | 1 | þ | 49546382 |
| Components |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Flanged by Grooved | Tyco | cv-1fp |  |  | 4" | þ | 49546387 |
| Internal Date |
| 12/31/1969 |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Under Ship M-46 | 4" | Open | Supervised | þ | 49546383 |
| Description |
| Main Control |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| System Sensor | OSY2 | 210 | NA |  | þ | 49546385 |
| Location |
| Under Ship |
| Devices |
| Drain |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | Under Ship | 2" | 210 |  |  |  | þ | 49546386 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | Under Ship | 2" | 165 | 165 | 00 |  | þ | 49546386 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | Under Ship | 2" | 165 | 165 | 00 |  | þ | 49546386 |
| Gauge |
| Location | Service Date |
| Under Ship | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | System Sensor | OSY2 | 210 | NA | 1/4 | þ | 49546392 |
| Gauge |
| Location | Service Date |
| Under Ship | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | System Sensor | OSY2 | 212 | NA | 1/4 | þ | 49546391 |
| Special Sprinkler |
| Qty | Type | KFactor | Finish | Temperature | OK | ScanID |
| 9 | Recessed Pendant |  | Brass | 155 | ¨ | 1 |
| Location | Description | Coverage |
| Under Ship | Quick Response |  |
| Sprinkler Box |
| Qty | Tool Available? | SIN List? | Size | Manufacturer | Location | OK | ScanID |
| 7 | No |  | 3 unit | unknown | Under Ship | ¨ | 49546390 |
| Sprinkler Box Spares |
| Qty | Type | Manufacturer | Location | OK | ScanID |
| 7 | Pendant | Tyco | Under Ship | ¨ | 49546389 |
| Temperature | KFactor | Size | Finish | Response Time |
| 175 | 5.6 |  | White | Standard Response |
| Wrenches |
| Qty | Type | Manufacturer | Location | OK | ScanID |
| 0 | Sprinkler | unknown | Under Ship | ¨ | 49546388 |

| Building: TAMPA SPORTS AUTHORITY | Quad A |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546397 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546405 |
| Control Valve | Supervisory | Kennedy | 1-2 75 | þ | 49546570 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546316 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546329 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546331 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546338 |
| Control Valve | Supervisory | Kennedy | 1-76 | þ | 46957762 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | System Sensor | WFD40 |  | 4” | 1 | þ | 49546394 |
| Vane | Potter | VSR |  | 4” | 1 | þ | 49546566 |
| Vane | Potter | unknown |  | 4” | 1 | þ | 49546333 |
| Vane | Potter | unknown |  | 4” | 1 | þ | 49546332 |
| Vane | N\A | unknown |  | 2.5” | 1 | þ | 49546342 |
| Components |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Grooved | Tyco | cv-1fr |  | Supervised | 4" | þ | 49546395 |
| Internal Date |
| 08/05/2019 |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Grooved | Tyco | cv-1fr |  | Supervised | 4" | þ | 49546406 |
| Internal Date |
| 08/05/2019 |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Grooved | Tyco | cv-1fr |  | Supervised | 4" | þ | 49546571 |
| Internal Date |
| 12/31/1969 |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 2nd Quad A Main Concourse M1-51 | 4" | Open | Supervised | þ | 49546396 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 2nd Quad A Main Concourse M1-41 | 4" | Open | Supervised | þ | 49546404 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 7th Quad A Upper Concourse M2-75 | 4" | Open | Supervised | þ | 49546572 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Catering Warehouse Restroom / Kitchen M1- | 4" | Open | Supervised | þ | 49546314 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Undeveloped Space M1-21 | 4" | Open | Supervised | þ | 49546328 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Undeveloped Space M1-19 | 4" | Open | Supervised | þ | 49546330 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Owners Parking M1-16 | 2.5" | Open | Supervised | þ | 49546339 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Catering Warehouse M1-76 | 4" | Open | Supervised | þ | 46957763 |
| Description |
| Main Control |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| N\A | unknown | 220 | NA |  | þ | 49546337 |
| Location |
| Quad A Owners Parking |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown | unknown | 0 |  | ¨ | 49546334 |
| Location |
| Quad A Undeveloped Space M1-19 |
| Devices |
| Drain |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 210 |  | 0 |  | þ | 49546398 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 165 | 165 | 0 |  | þ | 49546398 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 165 | 165 | 0 |  | þ | 49546398 |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 210 |  | 0 |  | þ | 49546407 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 165 | 165 | 0 |  | þ | 49546407 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad A Main Concourse M1-41 | 2" | 165 | 165 | 0 |  | þ | 49546407 |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad A Upper Concourse | 2" | 180 |  | 0 |  | þ | 49546567 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad A Upper Concourse | 2" | 135 | 134 | 0 |  | þ | 49546567 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad A Upper Concourse | 2" | 135 | 134 | 0 |  | þ | 49546567 |
| Gauge |
| Location | Service Date |
| 2nd Quad A Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 210 | NA | 1/4 | þ | 49546400 |
| Gauge |
| Location | Service Date |
| 2nd Quad A Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | unknown | 210 | NA | 1/4 | þ | 49546399 |
| Gauge |
| Location | Service Date |
| 2nd Quad A Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 210 | NA | 1/4 | þ | 49546403 |
| Gauge |
| Location | Service Date |
| 2nd Quad A Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | unknown | 205 | NA | 1/4 | þ | 49546402 |
| Gauge |
| Location | Service Date |
| 7th Quad A Upper Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 180 | NA | 1/4 | þ | 49546569 |
| Gauge |
| Location | Service Date |
| 7th Quad A Upper Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | unknown | 188 | NA | 1/4 | þ | 49546568 |
| Gauge |
| Location | Service Date |
| Quad A Owners Parking | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Kennedy | unknown | 220 | NA | 1/4 | þ | 49546344 |
| Signage |
| Type | Location | OK | ScanID |
| Hydraulic Info | Quad A Owners Parking RJ Corridor | þ | 49546341 |
| Hydraulic Info | Quad A Owners Parking RJ Parking | þ | 49546340 |

| Building: TAMPA SPORTS AUTHORITY | Quad B |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546289 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546299 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546297 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546311 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546309 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546306 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | Potter | unknown |  | 3” | 1 | þ | 49546305 |
| Vane | Potter | unknown |  | 3” | 1 | þ | 49546609 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad B Engineering M1-33 | 3" | Open | Supervised | þ | 49546295 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad B Boiler M1-38 | 8" | Open | Supervised | þ | 49546298 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | NIBCO | unknown | Quad B Boiler M1-39 | 8" | Open | Supervised | þ | 49546296 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad B Food Vending M1-37 | 4" | Open | Supervised | þ | 49546308 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad B Food Vending M1-40 | 4" | Open | Supervised | þ | 49546310 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad B East Club/Suite Lobby Hall M1-35 | 2.5" | Open | Supervised | þ | 49546608 |
| Description |
| Main Control |

| Building: TAMPA SPORTS AUTHORITY | Quad C |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546515 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546525 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546603 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546371 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546374 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | System Sensor | WFD40 |  | 4” | 1 | þ | 49546522 |
| Vane | System Sensor | WFD40 |  | 4” | 1 | þ | 49546523 |
| Vane | Potter | VSR |  | 4” | 1 | þ | 49546599 |
| Vane | Kennedy | unknown |  | 3” | 1 | þ | 49546372 |
| Vane | N\A | unknown |  | 3” | 1 | þ | 49546375 |
| Components |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Grooved | Tyco | cv-1fr |  | Supervised | 4" | þ | 57507888 |
| Internal Date |
| 12/31/1969 |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Flanged by Grooved | Tyco | cf-1fr |  | Supervised | 4" | þ | 57507889 |
| Internal Date |
| 12/31/1969 |
| Alarm Valve |
| Type | Manufacturer | Model # | Position | Status | Size | OK | ScanID |
| Grooved | Tyco | cv-1f |  | Supervised | 4" | þ | 49546604 |
| Internal Date |
| 09/19/2019 |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 2nd Quad C Main Concourse M1-45 | 4" | Open | Supervised | þ | 49546514 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 2nd Quad C Main Concourse M1-45 | 4" | Open | Supervised | þ | 49546524 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 7th Quad C Upper Concourse M2-46 | 4" | Open | Supervised | þ | 49546602 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad C Grounds Crew Storage Cage M1-29 | 3" | Open | Supervised | þ | 49546370 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad C Grounds Crew Storage Cage M1-30 | 3" | Open | Supervised | þ | 49546373 |
| Description |
| Main Control |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| Potter | VSR | 145 | 10 |  | ¨ | 49546606 |
| Location |
| 7th Quad C Upper Concourse Men’s restroom 330-331 |
| Devices |
| Drain |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 210 |  | 0 |  | þ | 49546517 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 250 | 250 | 0 |  | þ | 49546517 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 220 | 220 | 0 |  | þ | 49546517 |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 210 |  | 0 |  | þ | 49546516 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 250 | 250 | 0 |  | þ | 49546516 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 2nd Quad C Main Concourse | 2" | 217 | 217 | 0 |  | þ | 49546516 |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad C Upper Concourse | 2" | 00 | 00 | 00 |  | þ | 49546605 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad C Upper Concourse | 2" | 00 | 00 | 00 |  | þ | 49546605 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | 7th Quad C Upper Concourse | 2" | 195 | 195 | 00 |  | þ | 49546605 |
| Gauge |
| Location | Service Date |
| 2nd Quad C Main Concourse | 09/08/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | WIKA | unknown | 225 | NA | 1/4 | þ | 49546520 |
| Gauge |
| Location | Service Date |
| 2nd Quad C Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | N\A | unknown | 210 | NA | 1/4 | þ | 49546521 |
| Gauge |
| Location | Service Date |
| 2nd Quad C Main Concourse | 09/08/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | WIKA | unknown | 210 | NA | 1/4 | þ | 49546519 |
| Gauge |
| Location | Service Date |
| 2nd Quad C Main Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | WIKA | unknown | 220 | NA | 1/4 | þ | 49546518 |
| Gauge |
| Location | Service Date |
| 7th Quad C Upper Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | 111.10sp.100 | 184 | NA | 1/4 | þ | 49546601 |
| Gauge |
| Location | Service Date |
| 7th Quad C Upper Concourse | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | 49546601 | 185 | NA | 1/4 | þ | 49546600 |

| Building: TAMPA SPORTS AUTHORITY | Quad D |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546349 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546358 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | System Sensor | WFD40 |  | 4” | 1 | þ | 49546401 |
| Vane | Kennedy | unknown |  | 3” | 1 | þ | 49546350 |
| Vane | N\A | unknown |  | 3” | 1 | þ | 49546359 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad D Roll Up Door M1-28 | 3" | Open | Supervised | þ | 49546348 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad D TSA Hall M-119 | 3" | Open | Supervised | þ | 49546357 |
| Description |
| Main Control |

| Building: TAMPA SPORTS AUTHORITY | field |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Devices |
| --- |
| Hose Connection |
| Location | Size | OK | ScanID |
| East sideline on field | Class I - 2.5" | þ | 57507509 |

| Building: TAMPA SPORTS AUTHORITY | sideline |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Hose Connection |
| --- |
| Location | Size | OK | ScanID |
| West sideline on field | Class I - 2.5" | þ | 57507508 |

Standpipe Systems

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY | Quad A |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546327 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546320 |
| OS&Y | Supervisory | Kennedy | 1 | þ | 49546323 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Housekeeping / Field Entry M1-9 | 4" | Open | Supervised | þ | 49546326 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad A Housekeeping / Ramp M1-50 | 4" | Open | Supervised | þ | 49546315 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad A Mechanical Room M1-22 | 6" | Open | Supervised | þ | 49546322 |
| Description |
| Main Control |
| Devices |
| Fire Dep't Connection |
| Location | Type | BallDrip | Rotating Swivels | Size | OK | ScanID |
| Quad A FDC | Siamese | unknown | Yes | unknown | ¨ | 49546380 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 2nd Quad A Main Concourse | Class I - 2.5" | þ | 49546393 |
| 4th Quad A Club Level | Class I - 2.5" | þ | 49546545 |
| 5th Quad A Lower Suite | Class I - 2.5" | þ | 49546546 |
| 6th Quad A Upper Suite | Class I - 2.5" | þ | 49546513 |
| 7th Quad A Upper Concourse | Class I - 2.5" | þ | 49546561 |
| Quad A Catering Warehouse | Class I - 2.5" | þ | 49546313 |
| Quad A Ramp | Class I - 2.5" | þ | 49546321 |
| Quad A Mechanical Room | Class I - 2.5" | þ | 49546324 |
| Quad A Players Corridor | Class I - 2.5" | þ | 49546335 |
| Quad A Field Entry | Class I - 2.5" | þ | 57508118 |

| Building: TAMPA SPORTS AUTHORITY | Quad B |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546301 |
| Control Valve | Supervisory | Potter | 1 | þ | 49546317 |
| Control Valve | Supervisory | Kennedy | 1 | ¨ | 49546304 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad B Delivery Swing Gate M1-49 | 4" | Open | Supervised | þ | 49546300 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad B Chiller M1-47 | 8" | Open | Supervised | þ | 49546319 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | N\A | unknown | Quad B East Club/Suite Lobby Hall M1-15 | 2.5" |  |  | ¨ | 49546303 |
| Description |
| Main Control |
| Devices |
| Fire Dep't Connection |
| Location | Type | BallDrip | Rotating Swivels | Size | OK | ScanID |
| Quad B FDC | Siamese | unknown | Yes | unknown | þ | 49546261 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 2nd Quad B Main Concourse | Class I - 2.5" | þ | 49546527 |
| 4th Quad B / C Club Level | Class I - 2.5" | þ | 49546573 |
| 4th Quad B Club Level | Class I - 2.5" | þ | 49546598 |
| 5th Quad B / C Lower Suite | Class I - 2.5" | þ | 49546581 |
| 5th Quad B Lower Suite | Class I - 2.5" | þ | 49546580 |
| 6th Quad B / C Ford Super Suite | Class I - 2.5" | þ | 49546588 |
| 6th Quad B Ford Super Suite Pantry / Stairway 2 | Class I - 2.5" | þ | 49546594 |
| 7th Quad B Upper Concourse | Class I - 2.5" | þ | 49546595 |
| Quad B Delivery Swing Gate | Class I - 2.5" | þ | 49546302 |
| Quad B Field Entry | Class I - 2.5" | þ | 49546312 |
| Quad B East Club/Suite Lobby Hall | Class I - 2.5" | þ | 49546307 |
| Quad B Chiller | Class I - 2.5" | þ | 49546318 |

| Building: TAMPA SPORTS AUTHORITY | Quad C |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546365 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546378 |
| OS&Y | Supervisory | Kennedy | 1 | þ | 49546368 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad C Tunnel / Grounds Crew M1-26 | 4" | Open | Supervised | þ | 49546364 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad C Middle Hall M1-24 | 2.5" | Open | Supervised | þ | 49546377 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad C Mechanical M1-34 | 6" | Open | Supervised | þ | 49546367 |
| Description |
| Main Control |
| Devices |
| Fire Dep't Connection |
| Location | Type | BallDrip | Rotating Swivels | Size | OK | ScanID |
| Quad C FDC | Siamese | unknown | Yes | unknown | þ | 49546381 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 2nd Quad C Main Concourse | Class I - 2.5" | þ | 49546526 |
| 4th Quad C Club Level | Class I - 2.5" | þ | 49546579 |
| 5th Quad C Lower Suite | Class I - 2.5" | þ | 49546587 |
| 6th Quad C Upper Suite | Class I - 2.5" | þ | 49546593 |
| 7th Quad C Upper Concourse | Class I - 2.5" | þ | 49546607 |
| Quad C Tunnel / Grounds Crew | Class I - 2.5" | þ | 57507887 |
| Quad C Mechanical | Class I - 2.5" | þ | 49546369 |
| Quad C Field Entry | Class I - 2.5" | þ | 49546363 |
| Quad C Middle Hall | Class I - 2.5" | þ | 49546376 |

| Building: TAMPA SPORTS AUTHORITY | Quad D |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546346 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546353 |
| OS&Y | Supervisory | Kennedy | 1 | þ | 49546355 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546362 |
| Control Valve | Supervisory | Kennedy | 1-1 104 | þ | 57508120 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad D Players Entrance M1-25 | 2" | Open | Supervised | þ | 49546345 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad D Roll Up Door M1-27 | 4" | Open | Supervised | þ | 49546351 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Quad D Mechanical M1-30 | 6" | Open | Supervised | þ | 49546354 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad D TSA Hall M1-29 | 4" | Open | Supervised | þ | 49546361 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Quad D Buccs Warehouse HR Door 2 locker | 6" | Open | Supervised | þ | 57508121 |
| Description |
| Isolation |
| Devices |
| Fire Dep't Connection |
| Location | Type | BallDrip | Rotating Swivels | Size | OK | ScanID |
| Quad D FDC | Siamese | unknown | Yes | unknown | þ | 49546379 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 2nd Quad D Main Concourse | Class I - 2.5" | þ | 49546413 |
| 4th Quad A / D Club Level | Class I - 2.5" | þ | 49546544 |
| 4th Quad D Club Level | Class I - 2.5" | þ | 49546543 |
| 5th Quad A / D Lower Suite | Class I - 2.5" | þ | 49546552 |
| 5th Quad D Lower Suite | Class I - 2.5" | þ | 49546553 |
| 6th Quad D | Class I - 2.5" | þ | 49546565 |
| 6th Quad A / D Press Box | Class I - 2.5" | þ | 49546559 |
| 6th Quad D Press Box | Class I - 2.5" | þ | 49546560 |
| Quad D Players Corridor | Class I - 2.5" | þ | 49546336 |
| Quad D Roll Up Door | Class I - 2.5" | þ | 49546352 |
| Quad D TSA Hall | Class I - 2.5" | þ | 49546360 |
| Quad D Field Entry | Class I - 2.5" | þ | 49546347 |
| Quad D Mechanical | Class I - 2.5" | þ | 49546356 |

| Building: TAMPA SPORTS AUTHORITY | Stairway #6 |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546530 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546533 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546576 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546583 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546589 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | Potter | VSR |  | 4" | 1 | þ | 49546577 |
| Vane | Potter | VSR |  | 4” | 1 | þ | 49546585 |
| Vane | Potter | VSR |  | 4" | 1 | þ | 49546592 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | 2nd Stairway #6 M2-15 | 8" | Open | Supervised | þ | 49546529 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 3rd Stairway #6 M2-14 | 4" | Open | Supervised | þ | 49546532 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 4th Stairway #7 M2-13 Club Level | 4" | Open | Supervised | þ | 49546575 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 5th Stairway #6 M2-24 Lower Suite | 4" | Open | Supervised | þ | 49546582 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 6th Stairway #6 M2-35 Upper Suite | 4" | Open | Supervised | þ | 49546590 |
| Description |
| Main Control |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown |  | 83 |  | þ | 49546574 |
| Location |
| 4th Stairway #6 Club Level |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown |  | NA |  | þ | 49546584 |
| Location |
| 5th Stairway #6 Lower Suite |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| AGF | unknown |  | NA |  | þ | 49546591 |
| Location |
| 6th Stairway #6 Upper Suite |
| Devices |
| Gauge |
| Location | Service Date |
| 7th Stairway #6 | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | WIKA | 111.10sp.100 | 185 | NA | 1/4 | þ | 49546597 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 1st Stairway #6 | Class I - 2.5" | þ | 49546528 |
| 3rd Stairway #6 | Class I - 2.5" | þ | 49546531 |
| 4th Stairway #6 | Class I - 2.5" | þ | 49546578 |
| 5th Stairway #6 | Class I - 2.5" | þ | 49546586 |
| 7th Stairway #6 | Class I - 2.5" | þ | 49546596 |

| Building: TAMPA SPORTS AUTHORITY | Stairway #7 |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Alarms |
| --- |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546409 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546412 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546535 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546548 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546555 |
| Control Valve | Supervisory | Kennedy | 1 | ¨ | 49546541 |
| Waterflow Switch |
| Type | Manufacturer | Model # | Sec | Size | Zone/Address | OK | ScanID |
| Vane | Potter | VSR |  | 4" | 1 | þ | 49546537 |
| Vane | Potter | VSR |  | 4” | 1 | þ | 49546549 |
| Vane | Potter | VSR |  | 4" | 1 | þ | 49546557 |
| Vane | unknown | unknown |  | 4" | 1 | ¨ | 57508117 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 2nd Stairway #7 M2-5 | 8" | Open | Supervised | þ | 49546408 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 3rd Stairway #7 M2-29 | 4" | Open | Supervised | þ | 49546411 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 4th Stairway #7 M2-7 Club Level | 4" | Open | Supervised | þ | 49546534 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 4th Stairway #7 M2-99 Atrium | 4" | Open | Supervised | þ | 49546540 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 5th Stairway #7 M2-7 Lower Suite | 4" | Open | Supervised | þ | 49546547 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | 6th Stairway #7 M2-57 Upper Suite | 4" | Open | Supervised | þ | 49546554 |
| Description |
| Main Control |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown | 200 | NA |  | þ | 49546536 |
| Location |
| 4th Stairway #7 Club Level |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown |  | NA |  | þ | 49546550 |
| Location |
| 5th Stairway #7 Lower Suite |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| AGF | M1000 |  | NA |  | þ | 49546556 |
| Location |
| 6th Stairway #7 Upper Suite |
| Inspector's Test |
| Manufacturer | Model # | Pressure psi | Valve Trip Time sec | Water Flow Time sec | OK | ScanID |
| unknown | unknown | 150 | 41 |  | ¨ | 49546538 |
| Location |
| 4th Stairway #7 M2-99 Atrium |
| Devices |
| Gauge |
| Location | Service Date |
| 4th Stairway #7 M2-99 Atrium | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | unknown | unknown | 200 | NA | 1/4 | þ | 57508116 |
| Gauge |
| Location | Service Date |
| 7th Stairway #7 | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | unknown | unknown | 185 | NA | 1/4 | þ | 49546564 |
| Hose Connection |
| Location | Size | OK | ScanID |
| 5th Stairway #7 | Class I - 2.5" | þ | 49546551 |
| 6th Stairway #7 | Class I - 2.5" | þ | 49546558 |
| 7th Stairway #7 | Class I - 2.5" | þ | 49546562 |
| 7th Stairway #7 | Class I - 2.5" | þ | 49546563 |
| 1st Stairway #7 | Class I - 2.5" | ¨ | 49546410 |

Private Fire Service Mains

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |  |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Private Fire Service Main and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Devices |
| --- |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Southeast | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508122 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1060 | 44 | 40 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Northeast | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508123 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1130 | 56 | 46 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Quad B | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508124 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1130 | 54 | 44 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Quad A | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508125 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1000 | 54 | 40 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Quad A | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508126 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1060 | 54 | 40 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| West Hyundai Club | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508127 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1060 | 50 | 41 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| West team store | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508128 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1000 | 58 | 41 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Quad D | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508129 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1060 | 59 | 40 | Closed against pressure | 09/08/2020 |
| Fire Hydrant |
| Location | Mfr | Model | Type | Position | Size | OK | ScanID |
| Quad C | Clow | AWWA | Dry Barrel/Ground |  | 5.25” | ¨ | 57508130 |
| Description | Orifice | Flow Rate | Static | Residual | Valve Type | Flush Test Date |
| 1000 gpm/3786 lpm | 2@2-1/2" and 1@4 1/2" | 1060 | 52 | 40 | Closed against pressure | 09/08/2020 |

Preaction Fire Sprinkler Systems

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY | Control Room |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Preaction System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Air Compressor |
| --- |
| Location | Mfr. | Model # | Phase | On psi | Off psi | Serial No. |
| Control Room Low Air | Gast | unknown | 1 | unknown | 12 | N\A |
| Type | Description | Rated Speed | Horsepower | Volts | Amps | OK | ScanID |
| Automatic | Tank | 1725 | 1/6 | 115 | 3.5 | þ | 49546426 |
| Air Maintenance Device |
| Type | Model # | Location | Install Date | Air Pressure | ScanID |
| Pressure Reducing | unknown | Control Room | 01/01/1998 | 10 | 49546423 |
| Alarms |
| Pressure Switch |
| Type | Description | Manufacturer | Low | High | Zone/Address | OK | ScanID |
| Pressure Switch | Alarm | System Sensor | n/a | n/a | 1 | þ | 49546422 |
| Pressure Switch | Supervisory | System Sensor | n/a | n/a | 1 | þ | 49546421 |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| Control Valve | Supervisory | System Sensor | 1 | þ | 49546420 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | System Sensor | EPS10-2 | Upper Suite A Control Room Main Control | 2.5" | Open | Supervised | þ | 49546419 |
| Description |
| Main Control |
| Preaction Valve |
| Manufacturer | Model # | Serial # | Size | OK | ScanID |
| Reliable | DDX | unknown | 2.5" | þ | 49546262 |
| Type | Position | Status | Location | Solenoid | Timing (sec) |
| Double Interlock |  | Supervised | Control Room | 24vdc |  |
| Water psi | Air Pressure | Trip Air psi | Trip Time |
| 190 | 10 | n/a | n/a |
| Devices |
| Drain |
| Current Inspection |
| Type | Location | Size | Supply psi | Restored psi | Residual psi | Sec | OK | ScanID |
| Main | Control Room | 1.25" | 190 |  | n/a |  | þ | 49546425 |
| Previous Inspections |
| September 8, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | Control Room | 1.25" | 175 | 175 | n/a |  | þ | 49546425 |
| June 2, 2020 |
| Type | Location | Size | Supply psi | Static psi | Residual psi | Sec | OK | ScanID |
| Main | Control Room | 1.25" | 175 | 175 | n/a |  | þ | 49546425 |
| Gauge |
| Location | Service Date |
| Control Room | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Air Pressure | Wika | unknown | 10 | n/a | 1/4 | þ | 49546427 |
| Gauge |
| Location | Service Date |
| Control Room | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | unknown | 190 | n/a | 1/4 | þ | 49546415 |
| Gauge |
| Location | Service Date |
| Control Room | 09/08/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| System Pressure | Wika | unknown | 190 | n/a | 1/4 | þ | 49546416 |
| Gauge |
| Location | Service Date |
| Control Room | 09/08/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Air Pressure | Wika | unknown | 8 | n/a | 1/4 | þ | 49546417 |
| Gauge |
| Location | Service Date |
| Control Room | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Air Pressure | Wika | unknown | 10 | n/a | 1/4 | þ | 49546418 |
| Gauge |
| Location | Service Date |
| Control Room | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Air Pressure | Wika | unknown | 10 | n/a | 1/4 | þ | 49546424 |

Fire Pump Testing

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |  |
| --- | --- |
| This section lists out all the devices and components that have been associated with a Fire Pump and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section. |

| Controller |
| --- |
| Manufacturer | Model # | Location | Install Date | Serial Number |
| Master | mcttz225-125-46-fx | Pump Room | 01/22/2015 | 78756 |
| AC Power | Time Meter | Start psi | Stop psi | Battery Supervised | Generator Backup |
|  |  | 155 |  | No | Yes |
| Electrical |
| Manufacturer | Model # | Location | Serial Number | ScanID |
| U.S. Electrical Moto | H632 | Fire Pump Room | H632-A11A260R150M | 57507886 |
| Timing Min/Sec |  |
| Full | Run | Volts | Amps | Horsepower | Rated Speed |
|  |  | 460 | 137 | 125 | 3565 |
| Fire Pump Gauge |
| Location | Discharge psi | Suction psi | OK | ScanID |
| Jockey Pump Discharge |  | 50 | þ | 49546266 |
| Jockey Pump Discharge | 56 |  | þ | 49546277 |
| Controller |
| Manufacturer | Model # | Location | Install Date | Serial Number |
| Master | pic-3-3-46-12 | Jockey Pump Controller | 01/22/2015 | 78756 |
| AC Power | Time Meter | Start psi | Stop psi | Battery Supervised | Generator Backup |
|  |  | 150 | 170 | No | No |
| Jockey Pump |
| Manufacturer | Model Number | Location | Install Date | Scan Number |
| Baldor | 84.z00011 | Fire Pump Room | 01/22/2015 | 57507884 |
| Serial Number | Type | Horse Pwr | Rated Spd | Volts | Amps | On psi | Off psi |
| n/a | Automatic | 3 | 3540 | 208-230/460 | 8.4-8/4 | 150 | 170 |
| Pump |
| Manufacturer | Model Number | Location | Install Date | Scan Number |
| Patterson | 6x5 MAAH | Fire Pump Room | 01/01/1998 | 57507885 |
| Serial Number | Type | Orientation | Aligned? | Water Supply | Impeller Size |
| FP-c12613 | Pump Primary | Horizontal | Yes | Municipal | 9.50 |
| Alarms |
| Tamper Switch |
| Type | Description | Manufacturer | Zone/Address | OK | ScanID |
| OS&Y | Supervisory | Potter | 1 | þ | 49546264 |
| OS&Y | Supervisory | Potter | 1 | þ | 49546275 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546282 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546287 |
| Control Valve | Supervisory | Kennedy | 1 | þ | 49546343 |
| Components |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Fire Pump Suction | 8" | Open | Supervised | þ | 49546263 |
| Description |
| Suction |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Kennedy | unknown | Fire Pump Test Header | 8" | Closed | Supervised | þ | 49546274 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | United | unknown | Jockey Pump Discharge | 1.25" | Open |  | þ | 49546280 |
| Description |
| Main Control |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Fire Pump Discharge | 8" | Open | Supervised | þ | 49546281 |
| Description |
| Discharge |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| OS&Y | Wika | unknown | Jockey Pump Suction | 1.25" | Open |  | þ | 49546268 |
| Description |
| Isolation |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Fire Pump Bypass | 8" | Open | Supervised | þ | 49546285 |
| Description |
| Bypass |
| Control Valve |
| Type | Manufacturer | Model | Location | Size | Position | Status | OK | ScanID |
| Butterfly | Kennedy | unknown | Fire Pump Bypass | 8" | Open | Supervised | þ | 49546284 |
| Description |
| Bypass |
| Devices |
| Gauge |
| Location | Service Date |
| Fire Pump Controller | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 222 | NA | 1/4 | þ | 49546267 |
| Gauge |
| Location | Service Date |
| Fire Pump Relief Valve | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | 111.10sp.100 | 50 | NA | 1/4 | þ | 49546288 |
| Gauge |
| Location | Service Date |
| Fire Pump Relief Valve | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | 111.10sp.100 | 222 | NA | 1/4 | þ | 49546276 |
| Gauge |
| Location | Service Date |
| Jockey Pump Discharge | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | 111.10sp.100 | 60 | NA | 1/4 | þ | 49546290 |
| Gauge |
| Location | Service Date |
| Jockey Pump Controller | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | 111.10sp.100 | 222 | NA | 1/4 | þ | 49546278 |
| Gauge |
| Location | Service Date |
| Jockey Pump Suction | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 60 | NA | 1/4 | þ | 49546283 |
| Gauge |
| Location | Service Date |
| Jockey Pump Controller | 12/22/2020 |
| Type | Manufacturer | Model # | Static psi | Fill Type | Size | OK | ScanID |
| Supply Pressure | Wika | unknown | 225 | NA | 1/4 | þ | 49546273 |
| Signage |
| Type | Location | OK | ScanID |
| Hydraulic Info | Control Room | þ | 49546271 |
| Hydraulic Info | Home Team Locker Room | þ | 49546270 |
| Hydraulic Info | Team Store Atrium | þ | 49546269 |

Signage Report

Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY

This section documents a list of signage applicable to the system(s) in this building.

| Signage |
| --- |
| Type | Location | OK | ScanID |
| Hydraulic Info | Control Room | þ | 49546271 |
| Hydraulic Info | Home Team Locker Room | þ | 49546270 |
| Hydraulic Info | Team Store Atrium | þ | 49546269 |
| Hydraulic Info | Quad A Owners Parking RJ Corridor | þ | 49546341 |
| Hydraulic Info | Quad A Owners Parking RJ Parking | þ | 49546340 |

Inventory & Warranty Report

Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY

The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.

| Device or Type | Category | % of Inventory | Quantity |
| --- | --- | --- | --- |
| Special Sprinkler | Sprinkler | 0.36% | 1 |
| Inspector's Test | Valve | 4.27% | 12 |
| Control Valve | Valve | 19.57% | 55 |
| Tamper Switch | Alarm | 18.86% | 53 |
| Wrenches | Sprinkler | 0.36% | 1 |
| Sprinkler Box Spares | Sprinkler | 0.36% | 1 |
| Sprinkler Box | Sprinkler | 0.36% | 1 |
| Fire Hydrant | Hose | 3.20% | 9 |
| Waterflow Switch | Alarm | 8.54% | 24 |
| Fire Dep't Connection | Hose | 1.42% | 4 |
| Gauge | Device | 11.03% | 31 |
| Controller | Pump | 0.36% | 1 |
| Electrical Driver | Pump | 0.36% | 1 |
| Fire Pump Gauge | Pump | 0.71% | 2 |
| Jockey Pump | Pump | 0.36% | 1 |
| Jockey Controller | Pump | 0.36% | 1 |
| Hose Connection | Hose | 19.93% | 56 |
| Signage | Sprinkler | 1.78% | 5 |
| Alarm Valve | Valve | 2.49% | 7 |
| Drain | Device | 2.85% | 8 |
| Control Panel | Alarm | 0.36% | 1 |
| Preaction Valve | Valve | 0.36% | 1 |
| Pressure Switch | Alarm | 0.71% | 2 |
| Air Maintenance Device | Pump | 0.36% | 1 |
| Air Compressor | Pump | 0.36% | 1 |
| Pump | Pump | 0.36% | 1 |

| Device Type | Qty | Model # | Type | Description | Install Date |
| --- | --- | --- | --- | --- | --- |
| In Service - 90 Days - 1 Year |
| Fire Pump |
| Fire Pump Gauge | 1 | unknown | Suction |  | 03/04/2020 |
| Fire Pump Gauge | 1 | 111.10sp.100 | Discharge |  | 03/04/2020 |
| Gauge | 4 | 111.10sp.100 | Supply Pressure |  | 03/04/2020 |
| Gauge | 2 | unknown | Supply Pressure |  | 03/04/2020 |
| Preaction, Control Room |
| Gauge | 4 | unknown | Air Pressure |  | 03/04/2020 |
| Gauge | 2 | unknown | System Pressure |  | 03/04/2020 |
| Standpipe, Stairway #7 |
| Gauge | 1 | unknown | System Pressure |  | 03/04/2020 |
| Wet Pipe, Pirate Ship |
| Gauge | 1 | OSY2 | Supply Pressure |  | 03/04/2020 |
| Gauge | 1 | OSY2 | System Pressure |  | 03/04/2020 |
| Wet Pipe, Quad A |
| Gauge | 1 | unknown | System Pressure |  | 03/04/2020 |
| Gauge | 3 | unknown | Supply Pressure |  | 03/04/2020 |
| Gauge | 3 | unknown | System Pressure |  | 03/04/2020 |
| Wet Pipe, Quad C |
| Gauge | 1 | unknown | Supply Pressure |  | 03/04/2020 |
| Gauge | 1 | 111.10sp.100 | Supply Pressure |  | 03/04/2020 |
| Gauge | 1 | 49546601 | System Pressure |  | 03/04/2020 |
| Gauge | 1 | unknown | Supply Pressure |  | 03/04/2020 |
| Gauge | 2 | unknown | System Pressure |  | 03/04/2020 |
| In Service - 5 Years to 10 Years |
| Fire Pump |
| Jockey Pump | 1 | 84.z00011 | Automatic |  | 01/22/2015 |
| Controller | 1 | mcttz225-125-46-fx |  | Automatic | 01/22/2015 |
| Jockey Controller | 1 | pic-3-3-46-12 |  |  | 01/22/2015 |
| Signage | 3 | unknown | Hydraulic Info |  | 01/22/2015 |
| Control Valve | 1 | unknown | OS&Y | Isolation | 01/22/2015 |
| Gauge | 1 | unknown | Supply Pressure |  | 01/22/2015 |
| Standpipe, Stairway #6 |
| Gauge | 1 | 111.10sp.100 | System Pressure |  | 01/22/2015 |
| Wet Pipe, Quad A |
| Signage | 1 | unknown | Hydraulic Info |  | 01/22/2015 |
| Signage | 1 | unknown | Hydraulic Info |  | 01/22/2015 |
| Alarm Valve | 2 | cv-1fr | Grooved |  | 01/22/2015 |
| Wet Pipe, Quad C |
| Alarm Valve | 1 | cv-1f | Grooved |  | 01/22/2015 |
| In Service - 15 Years to 25 Years |
| Fire Pump |
| Control Valve | 2 | unknown | Butterfly | Bypass | 01/01/1998 |
| Control Valve | 1 | unknown | Butterfly | Discharge | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Suction | 01/01/1998 |
| Tamper Switch | 3 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Pump | 1 | 6x5 MAAH | Pump Primary |  | 01/01/1998 |
| Tamper Switch | 2 | OSYSU-2 | OS&Y | Supervisory | 01/01/1998 |
| Electrical Driver | 1 | H632 |  |  | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Preaction, Control Room |
| Air Compressor | 1 | unknown | Automatic | Tank | 01/01/1998 |
| Control Panel | 1 | PFC-4410RC |  |  | 01/01/1998 |
| Preaction Valve | 1 | DDX | Double Interlock |  | 01/01/1998 |
| Control Valve | 1 | EPS10-2 | Butterfly | Main Control | 01/01/1998 |
| Pressure Switch | 1 | EPS10-2 | Pressure Switch | Alarm | 01/01/1998 |
| Pressure Switch | 1 | EPS10-2 | Pressure Switch | Supervisory | 01/01/1998 |
| Tamper Switch | 1 | EPS10-2 | Control Valve | Supervisory | 01/01/1998 |
| Air Maintenance Device | 1 | unknown | Pressure Reducing |  | 01/01/1998 |
| Drain | 1 | unknown | Main |  | 01/01/1998 |
| Service Main |
| Fire Hydrant | 9 | AWWA | Dry Barrel/Ground | 1000 gpm/3786 lpm | 01/01/1998 |
| Standpipe, Quad A |
| Control Valve | 2 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Tamper Switch | 2 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Tamper Switch | 1 | unknown | OS&Y | Supervisory | 01/01/1998 |
| Fire Dep't Connection | 1 | unknown | Siamese |  | 01/01/1998 |
| Hose Connection | 10 | unknown |  |  | 01/01/1998 |
| Standpipe, Quad B |
| Control Valve | 1 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Tamper Switch | 2 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Control Valve | 1 | unknown | Butterfly | Main Control | 01/01/1998 |
| Hose Connection | 1 | unknown |  |  | 01/01/1998 |
| Tamper Switch | 1 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Fire Dep't Connection | 1 | unknown | Siamese |  | 01/01/1998 |
| Hose Connection | 11 | unknown |  |  | 01/01/1998 |
| Standpipe, Quad C |
| Control Valve | 2 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Hose Connection | 2 | unknown |  |  | 01/01/1998 |
| Tamper Switch | 2 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Tamper Switch | 1 | unknown | OS&Y | Supervisory | 01/01/1998 |
| Fire Dep't Connection | 1 | unknown | Siamese |  | 01/01/1998 |
| Hose Connection | 7 | unknown |  |  | 01/01/1998 |
| Standpipe, Quad D |
| Control Valve | 1 | unknown | Butterfly | Isolation | 01/01/1998 |
| Control Valve | 2 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 2 | unknown | OS&Y | Main Control | 01/01/1998 |
| Tamper Switch | 4 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Tamper Switch | 1 | unknown | OS&Y | Supervisory | 01/01/1998 |
| Fire Dep't Connection | 1 | unknown | Siamese |  | 01/01/1998 |
| Hose Connection | 13 | unknown |  |  | 01/01/1998 |
| Standpipe, Stairway #6 |
| Inspector's Test | 1 | unknown |  |  | 01/01/1998 |
| Control Valve | 4 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Tamper Switch | 5 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Hose Connection | 1 | unknown |  |  | 01/01/1998 |
| Waterflow Switch | 3 | VSR | Vane | Alarm | 01/01/1998 |
| Hose Connection | 4 | unknown |  |  | 01/01/1998 |
| Inspector's Test | 2 | unknown |  |  | 01/01/1998 |
| Standpipe, Stairway #7 |
| Inspector's Test | 1 | M1000 |  |  | 01/01/1998 |
| Control Valve | 6 | unknown | Butterfly | Main Control | 01/01/1998 |
| Tamper Switch | 6 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Waterflow Switch | 3 | VSR | Vane | Alarm | 01/01/1998 |
| Gauge | 1 | unknown | System Pressure |  | 01/01/1998 |
| Hose Connection | 5 | unknown |  |  | 01/01/1998 |
| Inspector's Test | 3 | unknown |  |  | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Wet Pipe |
| Inspector's Test | 1 | unknown |  |  | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Wet Pipe, field |
| Hose Connection | 1 | unknown |  |  | 01/01/1998 |
| Wet Pipe, Pirate Ship |
| Control Valve | 1 | unknown | Butterfly | Main Control | 01/01/1998 |
| Waterflow Switch | 1 | OVSR | Vane | Alarm | 01/01/1998 |
| Drain | 1 | OSY2 | Main |  | 01/01/1998 |
| Inspector's Test | 1 | OSY2 |  |  | 01/01/1998 |
| Tamper Switch | 1 | OSY2 | OS&Y | Supervisory | 01/01/1998 |
| Alarm Valve | 1 | cv-1fp | Flanged by Grooved |  | 01/01/1998 |
| Special Sprinkler | 1 | 329 | Recessed Pendant | Quick Response | 01/01/1998 |
| Sprinkler Box Spares | 1 | 329 | Pendant |  | 01/01/1998 |
| Sprinkler Box | 1 | unknown |  |  | 01/01/1998 |
| Wrenches | 1 | unknown | Sprinkler |  | 01/01/1998 |
| Wet Pipe, Quad A |
| Control Valve | 8 | unknown | Butterfly | Main Control | 01/01/1998 |
| Drain | 2 | unknown | Main |  | 01/01/1998 |
| Tamper Switch | 8 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Inspector's Test | 1 | unknown |  |  | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 2 | unknown | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 1 | VSR | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 1 | WFD40 | Vane | Alarm | 01/01/1998 |
| Alarm Valve | 1 | cv-1fr | Grooved |  | 01/01/1998 |
| Drain | 1 | unknown | Main |  | 01/01/1998 |
| Inspector's Test | 1 | unknown |  |  | 01/01/1998 |
| Wet Pipe, Quad B |
| Control Valve | 4 | unknown | Butterfly | Main Control | 01/01/1998 |
| Control Valve | 1 | unknown | OS&Y | Main Control | 01/01/1998 |
| Tamper Switch | 6 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Control Valve | 1 | unknown | Butterfly | Main Control | 01/01/1998 |
| Waterflow Switch | 2 | unknown | Vane | Alarm | 01/01/1998 |
| Wet Pipe, Quad C |
| Control Valve | 5 | unknown | Butterfly | Main Control | 01/01/1998 |
| Tamper Switch | 5 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Inspector's Test | 1 | VSR |  |  | 01/01/1998 |
| Waterflow Switch | 1 | VSR | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 2 | WFD40 | Vane | Alarm | 01/01/1998 |
| Alarm Valve | 1 | cf-1fr | Flanged by Grooved |  | 01/01/1998 |
| Alarm Valve | 1 | cv-1fr | Grooved |  | 01/01/1998 |
| Drain | 3 | unknown | Main |  | 01/01/1998 |
| Wet Pipe, Quad D |
| Control Valve | 2 | unknown | Butterfly | Main Control | 01/01/1998 |
| Tamper Switch | 2 | unknown | Control Valve | Supervisory | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 1 | unknown | Vane | Alarm | 01/01/1998 |
| Waterflow Switch | 1 | WFD40 | Vane | Alarm | 01/01/1998 |
| Wet Pipe, sideline |
| Hose Connection | 1 | unknown |  |  | 01/01/1998 |

Zone Address Report

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |
| --- |
| The Zone Address Report lists all of the devices and items that have an individual address, or are grouped together under a common zone. The device type, location and description are included for your reference. For more information on the device, use the link provided under ScanID. |
| Address | Device Type | Location | Type | ScanID |
| Control Panel 1 |
| Zone/Address: 1 |
| 104 | Control Valve | Quad D Buccs Warehouse HR Door 2 locker | Butterfly | 57508121 |
| 104 | Tamper Switch | Quad D Buccs Warehouse HR Door 2 locker | Control Valve | 57508120 |
| Zone/Address: 2 |
| 75 | Control Valve | 7th Quad A Upper Concourse M2-75 | Butterfly | 49546572 |
| 75 | Tamper Switch | 7th Quad A Upper Concourse M2-75 | Control Valve | 49546570 |
| Zone/Address: 3 |
| 33 | Control Valve | Upper Suite A Control Room Main Control | Butterfly | 49546419 |
| 76 | Control Valve | Quad A Catering Warehouse M1-76 | Butterfly | 46957763 |
| 76 | Tamper Switch | Quad A Catering Warehouse M1-76 | Control Valve | 46957762 |

Notes & Recommendations

Generated by: BuildingReports.com

| Building: TAMPA SPORTS AUTHORITY |
| --- |
| The Notes & Recommendations Report details additional inspection notes made by the Inspectors during the course of the building inspection. Notes are grouped by SystemID. |
| General Note |
| No Access to untested devices or not part of quarterly inspection. |
| Note | Device Type | Location | Comment | ScanID |
| Service Main |
| 2 | Fire Hydrant | Quad A |  | 57508125 |
| Missing blue road reflector and 2.5” cap |
| 3 | Fire Hydrant | West Hyundai Club |  | 57508127 |
| Missing Road marker Improper clearance around hydrant and to the ground needs 18” on both |
| Standpipe, Quad D |
| 4 | Control Valve | Quad D Roll Up Door M1-27 | Passed | 49546351 |
| Could not test due to missing chains see tamper device for M1- 27 for photos |
| Wet Pipe, Quad A |
| 5 | Tamper Switch | Quad A Catering Warehouse Restroom / Kitchen M1- | Passed | 49546316 |
| No tamper |